## Slide 1: Flint resident sampling: August 2015 vs. March 2016
Kelsey Pieper and Marc Edwards
Virginia Tech

## Slide 2: Flint residents
Dennis Walters, Matt Smith, Tracy Hacker, Tonya Williams, Kaylie Mosteller, Carrie Nelson, Claire McClinton, Keri Webber, Tony Palladeno Jr., Leah Palladeno, Jessica Owens

## Slide 3: Formation of scale within the distribution system
PO4-
Pb2+
PO4-
PO4-
PO4-
Pb2+
Pb2+
Pb2+
Pb2+
Flowing water
Lead-bearing
plumbing materials
Corrosion control
chemicals

## Slide 4: Formation of scale within the distribution system
Formation of protective scale
layer: requires flowing water
Flowing water

## Slide 5: Water from Flint River disrupted developed scales and biofilms
Flushing at low flow will clean lead
deposits very slowly: Maybe months to years
Loose lead and iron sediment in pipes

## Slide 6: Water from Flint River disrupted developed scales and biofilms
Flush pipes clean:
Remove lead and iron deposits in weeks
Flowing water

## Slide 7: Promote biofilm (bacteria) control
OCl-
OCl-
OCl-
OCl-
Flowing water
Chlorine disinfection can treat water
OCl-

## Slide 8: Comparing water quality in August 2015 vs. March 2016
To assess improvements since switch back to Detroit water and implementation of improved corrosion control

## Slide 9: Sampling protocol
Collected water samples from a cold water tap that is used for drinking water
1 L
First draw (FD)
500 mL
~1 min flush
250 mL
~3 min flush
Flush for
2 minutes
6+ hour stagnation
Flush for
45 seconds

## Slide 10: Homeowner sampling in Flint
August 2015: 269 homes sampled
  Participation rate: 90%
March 2016: 187 homes sampled
  Participation rate: 70%
174 homes participating
in both 2015 and 2016
used for analysis

## Slide 11: 174 households participated in both 2015 and 2016
 | Non detects | Average | Median | 90th | Max | % >AL
2015 |  |  |  |  |  | 
FD | 10% | 12.2 | 4.4 | 29.0 | 158 | 19%
1 min | 37% | 11.1 | 2.2 | 11.9 | 1,051 | 6%
3 min | 49% | 3.8 | 1.0 | 7.6 | 95 | 3%
2016 |  |  |  |  |  | 
FD | 38% | 32.3 | 1.8 | 23.0 | 2,253 | 15%
1 min | 58% | 3.6 | 0.5 | 9.0 | 81 | 5%
3 min | 71% | 1.9 | 0.5 | 3.4 | 69 | 2%

## Slide 12: 174 households participated in both 2015 and 2016
 | Non detects | Average | Median | 90th | Max | % >AL
2015 |  |  |  |  |  | 
FD | 10% | 12.2 | 4.4 | 29.0 | 158 | 19%
1 min | 37% | 11.1 | 2.2 | 11.9 | 1,051 | 6%
3 min | 49% | 3.8 | 1.0 | 7.6 | 95 | 3%
2016 |  |  |  |  |  | 
FD | 38% | 32.3 | 1.8 | 23.0 | 2,253 | 15%
1 min | 58% | 3.6 | 0.5 | 9.0 | 81 | 5%
3 min | 71% | 1.9 | 0.5 | 3.4 | 69 | 2%

## Slide 13: 174 households participated in both 2015 and 2016
 | Non detects | Average | Median | 90th | Max | % >AL
2015 |  |  |  |  |  | 
FD | 10% | 12.2 | 4.4 | 29.0 | 158 | 19%
1 min | 37% | 11.1 | 2.2 | 11.9 | 1,051 | 6%
3 min | 49% | 3.8 | 1.0 | 7.6 | 95 | 3%
2016 |  |  |  |  |  | 
FD | 38% | 32.3 | 1.8 | 23.0 | 2,253 | 15%
1 min | 58% | 3.6 | 0.5 | 9.0 | 81 | 5%
3 min | 71% | 1.9 | 0.5 | 3.4 | 69 | 2%

## Slide 14: 174 households participated in both 2015 and 2016
 | Non detects | Average | Median | 90th | Max | % >AL
2015 |  |  |  |  |  | 
FD | 10% | 12.2 | 4.4 | 29.0 | 158 | 19%
1 min | 37% | 11.1 | 2.2 | 11.9 | 1,051 | 6%
3 min | 49% | 3.8 | 1.0 | 7.6 | 95 | 3%
2016 |  |  |  |  |  | 
FD | 38% | 32.3 | 1.8 | 23.0 | 2,253 | 15%
1 min | 58% | 3.6 | 0.5 | 9.0 | 81 | 5%
3 min | 71% | 1.9 | 0.5 | 3.4 | 69 | 2%

## Slide 15: 174 households participated in both 2015 and 2016
 | Non detects | Average | Median | 90th | Max | % >AL
2015 |  |  |  |  |  | 
FD | 10% | 12.2 | 4.4 | 29.0 | 158 | 19%
1 min | 37% | 11.1 | 2.2 | 11.9 | 1,051 | 6%
3 min | 49% | 3.8 | 1.0 | 7.6 | 95 | 3%
2016 |  |  |  |  |  | 
FD | 38% | 32.3 | 1.8 | 23.0 | 2,253 | 15%
1 min | 58% | 3.6 | 0.5 | 9.0 | 81 | 5%
3 min | 71% | 1.9 | 0.5 | 3.4 | 69 | 2%

## Slide 16: 174 households participated in both 2015 and 2016
 | Non detects | Average | Median | 90th | Max | % >AL
2015 |  |  |  |  |  | 
FD | 10% | 12.2 | 4.4 | 29.0 | 158 | 19%
1 min | 37% | 11.1 | 2.2 | 11.9 | 1,051 | 6%
3 min | 49% | 3.8 | 1.0 | 7.6 | 95 | 3%
2016 |  |  |  |  |  | 
FD | 38% | 32.3 | 1.8 | 23.0 | 2,253 | 15%
1 min | 58% | 3.6 | 0.5 | 9.0 | 81 | 5%
3 min | 71% | 1.9 | 0.5 | 3.4 | 69 | 2%

## Slide 17: 2015 vs. 2016 first draws
Chart: 2015 first draw lead (ppb)
yaxis | 15 | 15
xaxis | 0.1 | 10000
1:1 line | 0.1 | 10000
10% >15 ppb in 2016 only
14% >15 ppb in 2015 only
5% >15 ppb in both years
15 ppb
15 ppb
1:1 line
71% <15 ppb in both years
Notes: Correlation

## Slide 18: 2015 vs. 2016 first draws
Chart: 2015 first draw lead (ppb)
No relationship between
lead levels by year
Recommending lead filters
17 ppb in 2015
2253 ppb in 2016
106 ppb in 2015
8 ppb in 2016
Notes: Correlation

## Slide 19: Iron in water concentrations
 | Average | Median | 90th | Max | %>SMCL
2015 |  |  |  |  | 
FD | 305.6 | 125.7 | 349.4 | 9,195 | 13%
1 min | 162.5 | 111.2 | 285.4 | 2,323 | 9%
3 min | 148.5 | 119.5 | 247.8 | 1,627 | 7%
2016 |  |  |  |  | 
FD | 292.7 | 53.7 | 418.4 | 13,820 | 14%
1 min | 92.9 | 36.3 | 157.2 | 1,471 | 5%
3 min | 83.0 | 40.5 | 160.6 | 1,572 | 4%

## Slide 20: Iron in water concentrations
 | Average | Median | 90th | Max | %>SMCL
2015 |  |  |  |  | 
FD | 305.6 | 125.7 | 349.4 | 9,195 | 13%
1 min | 162.5 | 111.2 | 285.4 | 2,323 | 9%
3 min | 148.5 | 119.5 | 247.8 | 1,627 | 7%
2016 |  |  |  |  | 
FD | 292.7 | 53.7 | 418.4 | 13,820 | 14%
1 min | 92.9 | 36.3 | 157.2 | 1,471 | 5%
3 min | 83.0 | 40.5 | 160.6 | 1,572 | 4%

## Slide 21: Iron in water concentrations
 | Average | Median | 90th | Max | %>SMCL
2015 |  |  |  |  | 
FD | 305.6 | 125.7 | 349.4 | 9,195 | 13%
1 min | 162.5 | 111.2 | 285.4 | 2,323 | 9%
3 min | 148.5 | 119.5 | 247.8 | 1,627 | 7%
2016 |  |  |  |  | 
FD | 292.7 | 53.7 | 418.4 | 13,820 | 14%
1 min | 92.9 | 36.3 | 157.2 | 1,471 | 5%
3 min | 83.0 | 40.5 | 160.6 | 1,572 | 4%

## Slide 22: Phosphate levels in 2016
Chart: Phosphate as P (ppm)
 | 0.1 | 10000
Detachment of leaded scale
Inadequate levels of corrosion control chemicals

## Slide 23: Change in lead levels by zip code
n=1
WTP

## Slide 24: Many Flint residents are using very little water
Two homes with persistent elevated lead problem only using 20-45% of typical monthly volume
Trying to reduce water bills
Showering only once per week (<5 min) to reduce the likelihood of rashes or exposure
Using bottled water for baths, washing dishes and other uses

## Slide 25: Conclusions
Flint is not yet meeting the 90%’ile lead action level
Lead levels are lower than in August 2015
Iron levels (and red water complaints) are decreasing
To speed up recovery of the system, residents will need to use more water

## Slide 26: Virginia Tech Research Team
Undergraduate Students: Madeleine Brouse, Margaret Carolan, Sara Chergaoui, Matthew Dowdle, Kim Hughes, Rebecca Jones, Alison Vick
Graduate Students: Christina Devine, Emily Garner, Catherine Grey, Pan Ji, Anurag Mantha, Rebekah Martin, Jake Metch, Victoria Nystrom, Colin Richards, William Rhoads, Siddhartha Roy, Laurel Strom, Owen Strom, Min Tang, Ni Zhu
Post-docs/Research Scientists: Brandi Clark, Dongjuan Dai, Sheldon Masters, Jeffrey Parks, David Schwake, Fei Wang
Virginia Tech Staff: Cassandra Hockman
Principal Investigators: Amy Pruden and Joseph Falkinham III

## Slide 27: Thank you!
Dennis Walters, Matt Smith, Tracy Hacker, Tonya Williams, Kaylie Mosteller, Carrie Nelson, Claire McClinton, Keri Webber, Tony Palladeno Jr., Leah Palladeno, Jessica Owens